## Costs
Price elements | Price in < currency to be inserted >
Price of luminaire with embedded Controllers
Price of the Controllers
Price of the Outdoor Lighting Network Communication Components
Price of the TALQ Gateway functionality (including licensing, hosting and maintenance if applicable)
Annual price for the Central Management Software as a Service (SaaS/Cloud) including upgrades, necessary daily maintenance, and remote technical support
Or
Price of an on-premises license of the Central Management Software
including yearly maintenance fees and specifications of the required hardware
If Service Level Agreements (SLAs) are offered to guarantee performance these should be outlined
Price for higher Service Level Agreement up to <please insert advanced SLA here (e.g., 99,95%)>
Price for additional data retention / storage < please indicate here the requested retention delay for specific information (e.g., detailed time series, energy data) >
On-site assistance service to help our team install the first < XXX > Controllers
Administrator Training Session
Full training about the solution
End-user Training Session
Full training about the solution
Development cost for any specific feature
Commissioning costs
Please list any additional costs related to communication, project management, risk management, escrow agreement settings,
Professional services for TALQ integration, onboarding, configuration, testing and commissioning
Please note: TALQ Certification ensures standardised interoperability interfaces between compliant systems. However, project-specific integration, configuration, validation and commissioning activities may still be required to achieve full operational interoperability within the deployed environment.
< Please add here other smart city and/or IoT elements that should be part of your tender >

## Controllers' Specifications
Item | Need | Specification | Mandatory / Optional | Supplier’s Compliance | Supplier’s explanation and comments
(Comply, Partly Comply, Not Comply)
5.B.1 | Certification | <Insert here the electronic and other certifications required in your country >
5.B.2 | Lifetime and warranty | <Insert here the expected lifetime and associated warranty for the Controllers >
5.B.3 | Identification of the Controllers, luminaires and drivers | Controllers shall be uniquely identified with a serial number that is reported to the CMS, and <optional> shall be able to read unique identifiers of the luminaire and the driver through the D4i protocol.
Where applicable, Controllers should support interoperable retrieval of luminaire, driver and sensor information through DALI D4i interfaces compliant with the DALI D4i TALQ Zhaga profiles.
5.B.4 | Type of installation | < Depending on your country and practices, you may require Controllers to be installed on ANSI 136.41 7-pin socket or ZhagaD4i connector or to be installed within the pole base or any other mechanism >
5.B.5 | Geographical positioning and auto-commissioning | < optional > Controllers shall be equipped with GPS chip and provide an auto-commissioning mechanism to avoid onsite operation at initial setup.
5.B.6 | Detect failures/events following the TALQ alarming functional test cases | Controllers shall have different detection capabilities of failures and events. Selection of required capabilities should be made, to detect failures/events such as:
- report lighting alarms to the CMS,
- report electrical alarms to the CMS
- report invalid program and calendar
that are logged on the Controller or in any other component of the Outdoor Lighting Network and sent to the CMS when relevant. Supplier shall list the failures/events supported by the proposed Controller, using the TALQ capability list, and shall describe how often and how fast these failures/events are sent to the CMS.
5.B.7 | Measure and log electrical values following the TALQ monitoring functional test cases called MONITOR-1 and MONITOR-6 | Controllers may have measurement capabilities of electrical values that can be logged in the Controller or in any other component of the Outdoor Lighting Network, to be sent to the CMS when relevant. Examples of such measurements are listed in the TALQ functional test cases: lamp level feedback, mains voltage, current, power consumption or power factor. Supplier shall list and assure the electrical values measured by the proposed Controller and shall describe how often, how accurately and how fast these data are measured and sent to the CMS.
5.B.8 | Provide energy and operating lamp hours following the TALQ monitoring functional test cases MONITOR-2, MONITOR-3, MONITOR-4 and MONITOR-5 | Controllers may measure the cumulative energy consumption (kWh) of the lamp, its number of operating hours number of switch-on and supply loss, log them in the Controller or in any other component of the Outdoor Lighting Network, to be sent to the CMS when relevant. Supplier shall describe how often, how accurate and how fast these data are measured and sent to the CMS.
5.B.9 | Provide mechanism to avoid data measurement to be lost | The proposed solution shall provide mechanisms to prevent from losing logged data. Supplier shall explain such mechanism when communication is lost between Controllers and other networking elements of the OLN.
5.B.10 | Run based on Control Program following the TALQ functional test cases PROGRAM-1 to PROGRAM-9 | Controllers shall accept and execute ON, OFF and dimming commands based on Control Programs and Calendars (including calendars with exception days) that are programmed by authorized end-users in the CMS and sent to the Controller through the Outdoor Lighting Network. Supplier should indicate if dimming is step-less or restricted to certain dimming values.
5.B.11 | Support dynamic light spectrum and colour temperature control | Where supported by the luminaires and drivers, Controllers shall support remote control of light spectrum and/or correlated colour temperature (CCT), including scheduled and adaptive operation intended to reduce adverse ‘Artificial Light at Night’ (ALAN) effects while maintaining lighting performance and safety requirements.
5.B.12 | Accept remote manual override following the TALQ functional test case called CONTROL-1 to CONTROL-7 | The Controller shall accept and execute remote manual override ON, OFF and dimming commands that are sent by authorized end-users in the CMS and sent to the Controller through the Outdoor Lighting Network. Supplier shall describe mechanisms, including queuing or losing commands, when end-to-end communication with Controller is lost.
5.B.13 | <optional> Asset Management information retrieved by Controllers and sent to CMS | <Please list here any additional feature related to specific asset management information that you require Controllers to retrieve from the D4i driver and send to the CMS. Examples may include luminaire manufacturer, luminaire type, driver information, operating parameters, diagnostics, energy data and sensor-related information retrieved through D4i interfaces.>
5.B.14 | <Optional if wider device connectivity is required> | The Controller/Network/CMS shall enable connectivity to additional devices/systems X, Y and Z. Supplier shall list any extra communication costs related to such use cases.
Serve as communication interface for Smart Cities and Internet of Things solutions
5.B.15 | <optional> Additional requirements specific to cabinet controllers | Where cabinet control functionality is proposed, cabinet controllers shall support reporting of cabinet alarms, feeder failures, power outages and abnormal electrical conditions to the CMS. Cabinet controllers shall support remote switching, scheduling and override commands through the TALQ protocol. The proposed solution should support autonomous operation based on internal schedules and/or astronomical clock functionality in case of communication loss with the CMS. Cabinet controllers should also support electrical measurements and energy monitoring relevant to outdoor lighting operations. The proposed cabinet control solution shall be TALQ-certified for the TALQ Cabinet Control Profile.

## Network Specifications
Item | Need | Specification | Mandatory / Optional | Supplier’s Compliance | Supplier’s explanation and comments
(Comply, Partly Comply, Not Comply)
5.C.1 | Interoperability & TALQ compliance | The proposed solution shall support interoperability through a TALQ Gateway compliant with the TALQ Smart City Protocol Version 2.7 (or above), enabling our organization to purchase and use a CMS from another vendor to control the Supplier’s Outdoor Lighting Networks (and associated Controllers) or other Outdoor Lighting Networks from other Suppliers.
The Outdoor Lighting Network shall apply TALQ Gateway functionality certified by the TALQ Consortium. A TALQ-compliant multi-vendor solution requires a TALQ Gateway acting as the standardized interoperability interface between the Outdoor Lighting Network and the CMS.
5.C.2 | Implement TALQ security requirements | The Outdoor Lighting Network shall implement the security mechanism recommended in the TALQ Technical Specification to secure the connection between the CMS and the Outdoor Lighting Network.
5.C.3 | Describe security within the OLN | Supplier shall describe in detail the security mechanisms in place between each hardware/software component, including Controllers, within the Outdoor Lighting Network.
5.C.4 | Device Addressing | The Outdoor Lighting Network shall assign a unique address to each logical device in its network and share it with the CMS, following the TALQ addressing convention.
5.C.5 | System upgrade | Please indicate if system can be upgraded / updated after installation, and how this is achieved through the TALQ protocol or not.
5.C.6 | <Specific communication technology> | <Please insert here the specific radiofrequency (or other) technology and/or protocol that you request the OLN solution to comply to>
5.C.7 | <Specific communication network performance level> | <Please specify here any specific network performance level that are required (e.g., max time to deploy a scheduler/calendar on all your light points, max time to get a given alarm, max time to deliver a manual override command>
5.C.8 | <optional> Dynamic sensor- based lighting | The OLN shall support dynamic sensor-based lighting with sensors, hooked on one given luminaire and connected to the OLN, shall trigger a light level change on a group of other luminaires controlled by Controllers connected to the same OLN. This capability shall also support ALAN mitigation strategies, including reduction of unnecessary light levels during low-activity periods, while maintaining safety and operational requirements. The proposed solution should also support seasonal and environmentally sensitive lighting strategies, including time-based, calendar-based or sensor-triggered operation intended to reduce ecological impact during wildlife-sensitive periods or in environmentally protected areas.

## CMS Specifications
Item | Need | Specification | Mandatory / Optional | Supplier’s Compliance | Supplier’s explanation and comments
(Comply, Partly Comply, Not Comply)
5.D.1 | Support OLN Control, Command and Monitoring | The CMS shall provide features and services such as remote command, remote control and remote monitoring of Controllers and any other available object (Supplier to describe) on the OLN.
5.D.2 | Commissioning and de-commissioning of Controllers | The CMS shall enable users to commission and de-commission any Controller and associated luminaires.
5.D.3 | <optional> Asset Management information | The CMS shall collect asset information read and reported by Controllers from the D4i drivers, to the CMS and provide related asset management features, including alerting and reporting.
Where supported by the deployed infrastructure, the CMS should support interoperable asset management capabilities enabled through the DALI D4i TALQ Zhaga profiles.
5.D.4 | Remote configuration of Controllers | The CMS shall enable users to remotely configure Controllers connected to the OLNs as per the description of the TALQ functional test cases CONFIG-1 to CONFIG-11.
5.D.5 | Remote Monitoring of Controllers | The CMS shall enable users to remotely monitor Controllers connected to the OLNs as per the description of the TALQ functional test cases MONITOR-1 to MONITOR-12.
5.D.6 | Remote Control of Controllers | The CMS shall enable users to remotely control Controllers connected to the OLNs as per the description of the TALQ functional test cases CONTROL-1 to CONTROL-7.
5.D.7 | Collect alarms from Controllers | The CMS shall collect and manage the alarms sent by Controllers connected to the OLNs as per the description of the TALQ functional test cases ALARM-1 to ALARM-5.
5.D.8 | Support outdoor lighting control program and calendars following the TALQ functional test cases PROGRAM-1 to 9 | The CMS shall provide outdoor lighting management features such remote programming (setting and deploying lighting control programs and calendars) through the TALQ Protocol.
5.D.9 | Spectrum-aware lighting management | The CMS shall support configuration, scheduling and monitoring of adaptive colour temperature and/or spectral lighting strategies where supported by the connected outdoor lighting infrastructure.
5.D.10 | Outdoor lighting management | The CMS shall provide data analytics, alarming, reporting and dashboarding features to turn all data and alarms and other monitoring features into energy and maintenance savings benefits.
5.D.11 | CMS operational expense model | < Please mention here the operational expense model you expect to use. >
5.D.12 | Security | Supplier shall describe the security measures and processes in place in or around the CMS to minimize security risks.
5.D.13 | GDPR compliancy | Supplier shall demonstrate its compliancy to GDPR principles.
5.D.14 | Licenses | The CMS shall not require 3rd party licenses or additional costs/prices not included in the Supplier’s pricing proposal.
5.D.15 | Backup and restore | The CMS shall provide backup and restore features, preferably in a physically separated location, to maximise the availability of the solution.
5.D.16 | Scalability and performance | The CMS shall be proven at comparable scale to this project. Supplier shall indicate the expected performance (e.g., response time for users, ability to collect massive amount of data).
5.D.17 | Support several Outdoor Lighting Networks | Supplier shall indicate any limitation of the number of TALQ-certified Outdoor Lighting Networks or OLN components the CMS can support.
5.D.18 | TALQ Certification | The CMS shall be certified by the TALQ Consortium for TALQ Version 2.7 (or above). The CMS shall support TALQ-certified outdoor lighting networks compatible since TALQ Version 2.1.
The TALQ testing process, certification process and certification test tools have been refined over several years to ensure interoperability and minimize risk for cities.
All officially TALQ-certified products can be found on the TALQ website
www.talq-consortium.org